## Slide 1
Dynamic Modeling and Simulation of a Power Plant Steam Condenser on the Siemens SPPA-T3000 Platform
Mohammad Odeh
Department of Mechanical and Aerospace Engineering
University of Central Florida
Committee Members
Dr. Tuhin Das
Dr. Tian Tian
Dr. Ranajay Ghosh
In collaboration with:

## Slide 2: Introduction
Motivation
  Improve current understanding
  Gain insight into transient operation and response to perturbation
  Fill gap in literature
Goal
  Develop and validate a dynamic condenser model
  Design the model such that it is generic (i.e. valid under any operational parameter)
  Predict condenser performance in near real-time operation

## Slide 3: Condensers
A subset of heat exchangers (HX)
  Shell-and-Tube design
Circulating water for cooling
  Freshwater, cooling tower
Extracts latent heat of vaporization
  Condensate forms on surface of tube bundles

## Slide 4: SPPA-T3000
Siemens Power Plant Automation T3000 (SPPA-T3000)
Visual Programming Language (VPL)
Equations consist of small building blocks
Embedded diagrams

## Slide 5: Model Formulation
Lumped Control Volume (CV) formulation
Three subsystems
  Metal CV
  Vapor CV
  Liquid CV
CV’s coupled with heat and mass transfer

## Slide 6: Metal Control Volume (CV)

## Slide 7: Metal CV – Formulation
Governing Equation (Energy balance):
Where,
Assumptions
  Cylindrical pipes
  Conduction only in the radial direction
  Quasi-static (avoid solving Fourier series and Bessel functions at every time-step)
  No fouling
  Constant properties (i.e. )
  Heat exchange with coolant at average inlet/outlet temperature
  Stainless-Steel 316

## Slide 8: Metal CV – Formulation
Under steady-state conditions (assumption used to compute cw outlet temperature for sake of simplicity),

## Slide 9: Metal CV – Formulation
Heat transfer from metal to cooling water (cw),
Cooling water (cw) outlet temperature is obtained from,
Re-arranging,

## Slide 10: Metal CV – Temperature Evolution
Temperature evolution found as follows,

## Slide 11: Vapor Control Volume (CV)

## Slide 12: Vapor CV – Formulation
Governing Equation (Energy balance):
Where internal energy is computed as,
And,
Assumptions
  Ideal gas
  At saturation
  No radiative heat transfer
  No non-condensables
  Filmwise condensation

## Slide 13: Vapor CV – Formulation
Governing Equation (Mass balance):
Expanding,

## Slide 14: Vapor CV – HTC Estimation
Where is the surface area,
Convective heat transfer coefficient ,
And,

## Slide 15: Vapor CV – HTC Estimation
The two-phase Reynolds number is defined as:
And the non-dimensional factor is,

## Slide 16: Vapor CV – HTC Estimation
The dynamic viscosity of the condensate film is approximated by:
, where
The thermal conductivity of the condensate film is approximated by:
, where
Where is the temperature of the condensate film:

## Slide 17: Vapor CV – Correction Factor
The effect of the superheat is usually small, but can be corrected for using the expression derived by Chen (1961):
Where,

## Slide 18: Vapor CV – Correction Factor
In accordance to the IAPWS 1955 formulation,
Where,

## Slide 19: Vapor CV – Temperature Evolution & Mass Transfer
Redefine Governing Equation:
Where,

## Slide 20: Vapor CV – Mode 1
Cooling mode:
Temperature drop
No mass transfer
Then,

## Slide 21: Vapor CV – Mode 2
Condensation mode:
Mass transfer @
Depressurization/Pressurization
Then,

## Slide 22: Vapor CV – Mode 2
Condensation mode – Oscillatory Response:

## Slide 23: Vapor CV – Mode 3
Heating-Condensing mode:
Incoming steam heats up vapor space
Now inside TS dome
Then,

## Slide 24: TS Diagram

## Slide 25: Vapor CV – Modes Summarized
Summary of 3 modes:
Where

## Slide 26: Vapor CV
The attemperation process involves de-superheating the steam down to about 3℃ (based on the engineer’s discretion) above its saturation temperature. The process can be modeled mathematically as follows,
Where is mass flow rate at which atomized coolant water is added into the stream path, is the enthalpy of the superheated steam, and is the desuperheated steam enthalpy.

## Slide 27: Liquid Control Volume (CV)

## Slide 28: Liquid CV – Formulation
Governing Equation (Energy balance):
Where internal energy is computed as,
And,
Assumptions
  Pure water
  Initially at CW temperature
  No heat transfer with the condenser hull.

## Slide 29: Liquid CV – Formulation
Governing Equation (Mass balance):
Expanding,

## Slide 30: Liquid CV – Temperature Evolution & Mass Transfer
Redefine Governing Equation:
Where,
In addition, note that,

## Slide 31: Liquid CV – Mode 1
Mass transfer constraint:
Variation in temperature
No mass transfer
Then,

## Slide 32: Liquid CV – Mode 2
Temperature constraint:
Flash steam generation (evaporation)
No variation in temperature
Then,

## Slide 33: Liquid CV – Volume Determination
Volume of CV determined as follows
The American Institute of Chemical Engineers (AIChE) proposed the following,
, where

## Slide 35: Results and Validation – Flash Steam

## Slide 36: Results and Validation – Mass Transfer

## Slide 37: Results and Validation – Temperature Evolution

## Slide 38: Results and Validation – Pressure Evolution

## Slide 39: Results and Validation – Comparison with Siemens Provided Data

## Slide 40: Results and Validation – Response to Perturbation

## Slide 41: Conclusion
A mathematical model of CCPP condenser was developed using SPPA-T3000
Model captures thermodynamics of system
  Logic switch between modes
Model was able to accurately predict performance.
  Showed good agreement with Siemens provided data
Demonstrated response to perturbation consistent with acceptable thermodynamic behavior
Implementation of time-varying quantities ensured validity over a wide range of inputs

## Slide 42: Future Research and Improvements
Resolve instability at low temperature/pressure operating conditions
Superheated steam HTC estimation
Attemperation
Implementation with HRSG, steam turbine, and pump models

## Slide 43: Thank you
In collaboration with: